## Title (hidden)
Appareil | Test | Test |  | Repos | Evacuation Afnor | Evacuation Afnor | Evacuation message | Evacuation message | Courant de pointe | Courant de pointe
| à vide | à pleine charge |  | à pleine charge | à vide | à pleine charge | à vide | à pleine charge | à vide | à pleine charge
VAS8
VAS16
VASLINE
PRO10
PRO20
PRO220
PRO40
PRO410
| Afnor | Message |  | Test | Repos
Temps (en min)
Ratio
Appareil | Pointe | Conso | Vide | avec groupe
VAS8
VAS16
VASLINE
PRO10
PRO20
PRO220
PRO40
PRO410
PRO10 sec
PRO20 sec
PRO40 sec

## Conso (hidden)
| 0.18 |  | 0.18 |  | 0.18 |  | 0.18 |  | 0.18
| 0.38 |  | 0.38 |  | 0.38 |  | 0.38 |  | 0.38
| 0.18 |  | 0.18 |  | 0.18 |  | 0.18 |  | 0.18
0.4 | 1.1 |  | 0.22 | 0.58 | 2.3 | 0.55 | 1.5 | 0.6 | 5
0.56 | 2.1 |  | 0.29 | 0.66 | 4.8 | 0.62 | 3 | 0.75 | 10
0.74 | 5.3 |  | 0.56 | 1.09 | 11 | 1.01 | 6.2 | 1.3 | 19
0.88 | 5.6 |  | 0.6 | 1.21 | 12 | 1.08 | 6.7 | 1.4 | 20
0.92 | 5.9 |  | 0.71 | 1.11 | 11.9 | 0.97 | 6.9 | 1.2 | 19
0.1 | 0.4 |  | 0.026667 | 1.33
0.18182 | 0.72727 |  | 0.019656 | 0.98034
0.18 | 2.7361 |  | 2.1889
0.38 | 5.7762 |  | 4.6209
0.18 | 2.7361 |  | 2.1889
5 | 3.7428 | 2.7437 | 2.9943
10 | 5.2386 | 3.6164 | 4.1909
19 | 10.5496 | 6.8881 | 8.4397
20 | 11.2882 | 7.4014 | 9.0306
19 | 13.0196 | 8.7057 | 10.4157
0.53 | 3.3996 |  | 2.7197
0.56 | 4.4911 |  | 3.5929
1.02 | 9.2091 |  | 7.3673

## How to use
Version3
05/20/2014
This Worksheet is used to calculate the Safety Power Supply with EN54-16 VAS Systems.
The calculation is made to have 12h05 in stand by mode and 5min in alarm mode full power, according to the NF-508
In the sheet"Calculation": |  | CALCULATION
| 1- Enter the number of device, |  |  | Part: | Green
| 2- Enter the total power of HP in your site in Watts, |  |  |  |  | Part: | Bleue
| 3- If the total power of HP in the site is less than the total power of amplifiers, "OK" will appear in the | [6 empty] | Part: | Yellow
In the other case, "Total Power HP is more important than the system" will appear because your configuration isn't correct.
| 4- In the part, | Grey | you have the number and the type of Power Supply to use,
If "Contact the technical departement" appears, your configuration need more than one Safety Power Supply.
In this case, contact the technical departement of MAJORCOM to adjust your system.
| 5- In the part, | Purple | you have the number and the type of battery needed.
If "Contact the technical departement" appear, your configuration need more than one Safety Power Supply.
In this case, contact the technical departement of MAJORCOM to adjust your system.

## Calculation
EN 54-16 VAS System
Site:
Products | Quantity |  |  |  | 12h05+5min (Ah vide)
VAS8 | 0 | 0 |  | 0 | 0
VAS16 | 0 | 0 |  | 0 | 0
VAS-LINE | 0 | 0 |  | 0 | 0
PRO10 | 0 | 0 | 0 | 0 | 0 |  | 0
PRO20 | 0 | 0 | 0 | 0 | 0 |  | 0
PRO220 | 0 | 0 | 0 | 0 | 0 |  | 0
PRO40 | 0 | 0 | 0 | 0 | 0 |  | 0
PRO410 | 0 | 0 | 0 | 0 | 0 |  | 0
PRO10 spare | 0 | 0 |  | 0 | 0
PRO20 s | 0 | 0 |  | 0 | 0
PRO40 secours | 0 | 0 |  | 0 | 0
|  | 0 | 0 | 0 | 0 |  | 1
Total Power HP | 0 | Watts |  | 0
-
12h05 stand by mode + 5min Alarm | 0.5 | A / Battery: |  | 2 |  | Ah
Results: | Quantity | Products
| 1 | AESRK 24V MS40
| 2 | Battery 24Ah